## AI Audit Data
SECTION: AHU Fan Audit (Format B)
Sr. | AHU Fan | Application | Design Flow, CFM | Static Pressure, MMWG | Measured Static Pressure, MMWG | Make | Frame Size | Foot or Flange Mounted | Rated Power, KW | Rated Efficiency, % | IE Class (IE1/IE2/IE3) | Rated RPM | VFD installed, (Y/N), Oper Hz & Make | Daily Running Hours Hrs/Day | Annual Operating Days, Days/Year | belt / direct driven | Phase (R/Y/B/Avg) | Measured Voltage | Measured Current | Measured KW | Measured PF
9 | PA/AHU 05 | Supply Air | 10500 | 140 |  |  |  |  | 11 |  |  |  | Yes, 50Hz, Danfoss | 24 | 353 | Belt | R | 422.2 | 11.8 | 7.897 | 0.997
[17 empty] | Y | 421.8 | 12.2 | 8.180 | 0.997
B
Avg
| PA/AHU 05 (Return) | Return Air | 9077 | 65 |  |  |  |  | 5.5 |  |  |  | Yes, 10Hz, Danfoss | 24 | 353 | Belt | R | 420.6 | 0.71 | 0.345 | 0.996
[17 empty] | Y | 417.9 | 1.15 | 0.518 | 0.996
B
Avg
| Heater | [7 empty] | 33 |  |  |  | Thyristor Fired (ON/OFF) |  |  |  | R
Y
B
Avg
10 | PA/AHU 07 | Supply Air | 6500 | 100 |  |  |  |  | 5.5 |  |  |  | Yes, Danfoss, 49.8 | 24 | 353 | Belt | R | 439 | 6.7 | 3.788 | 0.831
[17 empty] | Y | 432.5 | 6.62 | 3.691 | 0.834
B
Avg
| PA/AHU 07 (Return) | Return Air | 6500 | 65 |  |  |  |  | 2.2 |  |  |  | Yes, Danfoss, 28.5 Hz | 24 | 353 | Belt | R |  |  | 0.727
[17 empty] | Y |  |  | 0.679
B
Avg
1 | Heater | [7 empty] | 29 | [6 empty] | Thy | R | 416 | 9.34 | 3.126 | 0.999
Y
B
Avg
2 | PA AHU 04 | Supply Air | 7500 | 100 |  |  |  |  | 5.5 |  |  |  | Yes, 50Hz Danfoss | 24 | 353 | Belt | R | 434.2 | 7.36 | 3.916 | 0.790
[17 empty] | Y | 433.1 | 7.48 | 3.995 | 0.788
B
Avg
3 | PA AHU 04 | Return Air | 7500 | 65 |  |  |  |  | 3.7 |  |  |  | Yes, 19 Hz VLT | 24 | 353 | Belt | R |  |  | 0.447
[17 empty] | Y |  |  | 0.491
B
Avg
4 | PA AHU 12 | Supply Air C1007 | 5000 | 100 |  |  |  |  | 7.5 |  |  |  | Yes, 40Hz Danfoss | 24 | 353 | Belt | R | 388.3 | 7.84 | 2.978 | 0.907
[17 empty] | Y | 428 | 5.55 | 2.827 | 0.996
B
Avg
5 | PA AHU 13 | Supply Air C1008 | 5000 | 100 |  |  |  |  | 5.5 |  |  |  | Yes, 42.5 Hz Danfoss | 24 | 353 | Belt | R | 400.2 | 9.62 | 1.866 | 0.705
[17 empty] | Y | 403.8 | 4.87 | 1.198 | 0.706
B
Avg
1 | Heater | [7 empty] | 28.5 | [6 empty] | Thyristor Fbeg | R | 406.9 | 1.41 | 0.188 | 0.402
[17 empty] | Y | 406.8 | 1.18 | 0.195 | 0.739
B
Avg
2 | PAU AHU 03 | Supply Air | 6500 | 100 |  |  |  |  | 5.5 |  |  |  | Yes 50 Danfoss | 24 | 353 | Belt | R | 430.5 | 5.68 | 3.585 | 0.902
[17 empty] | Y | 432.5 | 5.59 | 2.388 | 0.908
B
Avg
2 | PAU AHU 03 (No Heater) | Return Air | 6500 | 65 |  |  |  |  | 3.7 |  |  |  | Yes 50.1 Hz | 24 | 353 | Belt | R |  |  | 0.282
[17 empty] | Y |  |  | 0.223
B
Avg
3 | PAU AHU 08 | Supply Air | 7500 | 140 |  |  |  |  | 9.3 |  |  |  | Yes 49.5 Danfoss | 24 | 353 | Belt | R | 434.1 | 9.55 | 4.19 | 0.766
[17 empty] | Y | 440.5 | 9.76 | 5.500 | 0.771
B
Avg
3 | PAU AHU 08 | Return Air | 7500 | 65 |  |  |  |  | 3.7 |  |  |  | Yes 26.5 Hz | 24 | 353 | Belt | R |  |  | 0.664
[17 empty] | Y |  |  | 0.570
B
Avg
1 | PA AHU 10 | Supply Air | 1500 | 100 | null | null | null | null | 1.5 | null | null | null | Yes, 48.5 Hz Danfoss | 24 | 353 | Belt | R | 434 | 1.57 | 0.94 | 0.838
null | null | null | null | null | null | null | null | null | null | null | null | null | null | null | null | null | Y | 434.2 | 1.62 | 0.768 | 0.754
null | null | null | null | null | null | null | null | null | null | null | null | null | null | null | null | null | B | null | null | null | null
null | null | null | null | null | null | null | null | null | null | null | null | null | null | null | null | null | Avg | null | null | null | null
null | null | Return Air | 1500 | 65 | null | null | null | null | 0.75 | null | null | null | Yes, Danfoss 29.8 Hz | 24 | 353 | Belt | R | null | null | null | null
null | null | null | null | null | null | null | null | null | null | null | null | null | null | null | null | null | Y | null | 0.199 | null | 0.153
null | null | null | null | null | null | null | null | null | null | null | null | null | null | null | null | null | B | null | null | null | null
null | null | null | null | null | null | null | null | null | null | null | null | null | null | null | null | null | Avg | null | null | null | null
null | null | Heater | null | null | null | null | null | null | 3 | null | null | null | null | null | null | Star | R | 402.3 | 3.42 | 1.978 | 0.914
null | null | null | null | null | null | null | null | null | null | null | null | null | null | null | null | null | Y | 393.3 | 3.15 | 1.739 | 0.903
null | null | null | null | null | null | null | null | null | null | null | null | null | null | null | null | null | B | null | null | null | null
null | null | null | null | null | null | null | null | null | null | null | null | null | null | null | null | null | Avg | null | null | null | null
2 | PA AHU 02 | Supply Air | 6600 | 100 | null | null | null | null | 11 | null | null | null | Yes, Danfoss 42.8 Hz | 24 | 353 | Belt | R | 422 | 7.20 | 4.419 | 0.993
null | null | null | null | null | null | null | null | null | null | null | null | null | null | null | null | null | Y | 430.8 | 8.14 | 4.843 | 0.980
null | null | null | null | null | null | null | null | null | null | null | null | null | null | null | null | null | B | 420.8 | 8.16 | 5.010 | 0.983
null | null | null | null | null | null | null | null | null | null | null | null | null | null | null | null | null | Avg | null | null | null | null
null | null | Return Air | 6600 | 65 | null | null | null | null | 3.7 | null | null | null | Yes, 41.9 Hz Danfoss | 24 | 353 | Belt | R | 420.2 | 0.75 | 0.330 | 0.998
null | null | null | null | null | null | null | null | null | null | null | null | null | null | null | null | null | Y | 416.9 | 1.01 | 0.512 | 0.999
null | null | null | null | null | null | null | null | null | null | null | null | null | null | null | null | null | B | null | null | null | null
null | null | null | null | null | null | null | null | null | null | null | null | null | null | null | null | null | Avg | null | null | null | null
1 |  | Return Air | 5500 | 65 |  |  |  |  | 3.7 |  |  |  | Yes, 29.4 Hz | 24 | 353 | Belt | R |  |  | 0.521
[17 empty] | Y |  |  | 0.484
B
Avg
2 |  | Heater | [6 empty] | 21 | [6 empty] | Thyristor | R | 404.3 | 5.60 | 1.735 | 0.688
[17 empty] | Y | 402.9 | 12.1 | 4.567 | 0.674
[17 empty] | B | 405.6 | 6.59 | 2.430 | 0.701
Avg
3 | PA AHU 11 | Supply Air | 1600 | 100 |  |  |  |  | 1.5 |  |  |  | Yes, 48.7 Hz | 24 | 353 | Belt | R | 442.7 | 2.07 | 1.326 | 0.832
[17 empty] | Y | 431.7 | 1.98 | 1.143 | 0.863
B
Avg
4 |  | Return Air | 1600 | 65 |  |  |  |  | 1.1 |  |  |  | Yes, 29.7 Hz | 24 | 353 | Belt | R |  |  | 0.334
[17 empty] | Y |  |  | 0.335
B
Avg
5 |  | Heater | [6 empty] | 3 | [6 empty] | Thyristor | R | 402.9 | 3.97 | 2.108 | 0.982
[17 empty] | Y | 404.1 | 3.69 | 2.268 | 0.962
[17 empty] | B | 400.7 | 3.58 | 2.330 | 0.978
Avg
1 | PA AHU 06 | Supply Air | 6400 | 140 |  |  |  |  | 9.3 |  |  |  | Yes 47.5 Hz Dan |  |  | Belt | R | 423 | 11.8 | 7.050 | 0.996
[17 empty] | Y | 423 | 12 | 7.999 | 0.992
B
Avg
2 | PA AHU 06 | Return Air | 6400 | 65 |  |  |  |  | 3.7 |  |  |  | Yes 38.9 Hz Dan |  |  | Belt | R | 422.2 | 1.16 | 0.800 | 0.998
[17 empty] | Y | 418.5 | 1.46 | 0.771 | 0.999
B
Avg
3 | Heater | [7 empty] | 22.5 | [7 empty] | R | 422.8 | 36 | 24.79 | 0.779
Y
B
Avg
4 | PA AHU 05 | Supply Air | 8000 | 100 |  |  |  |  | 18.5 |  |  |  | Yes 44 Hz Poly |  |  | Belt | R | 413.7 | 26.8 | 19.59 | 0.911
Y
B
Avg
5 | PA AHU 05 | Return Air | 8000 | 65 |  |  |  |  | 3.7 |  |  |  | Yes 26 Hz Dan |  |  | Belt | R | 420.8 | 2.92 | 1.307 | 0.995
[17 empty] | Y | 421.2 | 2.89 | 1.580 | 0.997
B
Avg
1 | Heater | [7 empty] | 12 KW | [6 empty] | Thyristor (OFF) | R
Y
B
Avg
2 | PA AHU 01 |  | 7500 | 100 |  |  |  |  | 11 |  |  |  | Yes 33Hz Danfoss |  |  | belt | R
Y
B
[17 empty] | Avg | 421.5 | 7.23 | 4.099 | 0.978
3 | 750 |  | 6500 | 65 |  |  |  |  | 3.7 |  |  |  | Yes 44.8 Hz Danfoss |  |  | belt | R
Y
B
[17 empty] | Avg | 418.9 | 1.33 | 0.792 | 1.000
1 | PC FDV 01 | Supply Air | 1500 | 60 | null | null | null | null | 0.75 | null | null | null | No | 24 | 333 | Belt | R | 423.8 | 2.47 | 1.201 | 0.702
[17 empty] | Y | 426.1 | 2.18 | 1.312 | 0.742
B
Avg
|  | Return Air | 1500 | 50 | null | null | null | null | 0.37 | null | null | null | No | 24 | 333 | Belt | R | Both Blower fan
Y
B
Avg
| PB AHU 04 | Supply Air | 7784 | null | null | null | null | null | 30 | null | null | null | Yes 33.3 Hz Danfoss | 24 | 333 | Belt | R | 423.1 | 12 | 6.452 | 0.985
[17 empty] | Y | 422.2 | 11.35 | 5.843 | 1.000
B
Avg
| PB AHU 03 | Supply Air | 19067 | null | null | null | null | null | 11 | null | null | null | Yes 35 Hz Danfoss | 24 | 333 | Belt | R |  |  | 1.95
Y
B
Avg
| PB AHU 02 | Supply Air | 12577 | null | null | null | null | null | 15 | null | null | null | Yes 51.5 Hz | 24 | 333 | Belt | R | 421.9 | 29.8 | 16.61 | 0.799
[17 empty] | Y | 426.8 | 24.5 | 16.54 | 0.796
B
Avg
PB | AHU 01 | Supply Air | 18290 | [5 empty] | 22 |  |  |  | Yes, ABB, 37 Hz | 24 | 353 | Belt | R | 421.2 | 8.91 | 4.729 | 0.999
[17 empty] | Y | 421.5 | 10.2 | 5.492 | 0.933
[17 empty] | B | 422.4 | 11.3 | 6.316 | 0.999
Avg
PB | Heater | [7 empty] | 48 | [7 empty] | R | 405 | 15.5 | 8.755 | 0.849
[17 empty] | Y | 402.1 | 11.8 | 5.188 | 0.790
B
Avg
PC | AHU 01 | Supply Air | 6500 | [5 empty] | 5.5 |  |  |  | Yes, Danfoss, 33 Hz | 24 | 353 | Belt | R | 424.9 | 3.3 | 1.916 | 0.991
[17 empty] | Y | 425.5 | 2.85 | 1.624 | 0.998
B
Avg
PC | AHU 01 | Return Air | [6 empty] | 3.7 |  |  |  | Yes, HL, Danfoss, 20 Hz | 24 | 353 | Belt | R | 420.3 | 1.29 | 0.589 | 0.926
[17 empty] | Y | 421.6 | 1.33 | 0.613 | 0.982
B
Avg
PC | AHU 04 | Supply Air | 7000 | 140 |  |  |  |  | 7.5 |  |  |  | Yes, Danfoss, 24 Hz | 24 | 353 | Belt | R | 421 | 10.1 | 5.784 | 0.769
[17 empty] | Y | 421.3 | 11.3 | 6.505 | 0.807
B
Avg
1 | PC AHU 03 | Return Air | 11450 | 65 |  |  |  |  | 5.5 |  |  |  | Yes, 35 Hz, Danfoss | 24 | 353 | Belt | R | 427.4 | 3.06 | 1.672 | 0.998
[17 empty] | Y | 423.5 | 3.02 | 1.658 | 0.997
B
Avg
2 | PC AHU 03 | Supply Air | 10500 | 140 |  |  |  |  | 15 |  |  |  | Yes, 29 Hz, Danfoss | 24 | 353 | Belt | R | 424.7 | 19.6 | 7.863 | 0.733
[17 empty] | Y | 420.1 | 16.6 | 8.551 | 0.729
B
Avg
3 | PC AHU 02 | Return Air | 11857 | 65 |  |  |  |  | 7.5 |  |  |  | Yes, 29 Hz, Danfoss | 24 | 353 | Belt | R | 424.4 | 8.28 | 4.969 | 0.828
[17 empty] | Y | 418.3 | 8.90 | 4.587 | 0.693
B
Avg
4 | PC AHU 02 | Heater | [6 empty] | 20.5 | [7 empty] | R | Thyristor (OFF)
Y
B
Avg
5 | PC AHU 02 | Supply Air | 3630 | [5 empty] | 5.5 |  |  |  | Yes, 32 Hz, Danfoss | 24 | 353 | Belt | R | 425.8 | 3.53 | 2.048 | 0.997
[17 empty] | Y | 421 | 3.61 | 2.094 | 1.000
B
Avg
01 | ST AHU 01 | Supply Air | 1500 | 140 |  |  |  |  | 2.2 |  |  |  | Yes 49.9 Hz | 24 | 353 | Belt | R | 421.2 | 1.77 | 1.325 | 1.000
[17 empty] | Y | 417.2 | 1.91 | 1.195 | 0.999
B
Avg
| Return Air | Return Air | 1200 | 65 |  |  |  |  | 1.1 |  |  |  | Yes 20Hz Danfoss | 24 | 353 | Belt | R | 422.2 | 0.83 | 0.183 | 0.903
Y
B
Avg
02 | ST AHU 02 | Supply Air | 1500 | 140 |  |  |  |  | 2.2 |  |  |  | Yes 50 Hz Danfoss | 24 | 353 | Belt | R | 424.1 | 2.26 | 1.571 | 1.000
[17 empty] | Y | 426.2 | 2.24 | 1.629 | 0.999
B
Avg
| Return Air | Return Air | 1077 | 65 |  |  |  |  | 1.1 |  |  |  | Yes 25 Hz Danfoss | 24 | 353 | Belt | R | 423.2 | 1.05 | 0.394 | 0.860
Y
B
Avg
03 | ST AHU 03 | Supply Air | 3000 | [5 empty] | 3.7 |  |  |  | N | 24 | 353 | Belt | R | 422.1 | 8.06 | 5.192 | 0.882
Y
B
Avg
1 | B AHU 07 | Supply Air | 8000 | 100 |  |  |  |  | 7.5 |  |  |  | Schneider 40 Hz | 24 | 353 | Belt | R | 409.3 | 3.37 | 2.095 | 0.990
[17 empty] | Y | 407.4 | 3.28 | 2.179 | 0.999
B
Avg
2 |  | Return Air | [6 empty] | 5.5 |  |  |  | Schneider 36 Hz | 24 | 353 | Belt | R | 405 | 2.54 | 1.079 | 0.625
[17 empty] | Y | 407.3 | 2.45 | 1.585 | 0.492
B
Avg
3 | B AHU 13 | Supply Air | 1500 | 100 |  |  |  |  | 1.5 |  |  |  | Schneider Yes 50 Hz | 24 | 353 | Belt | R | 409.8 | 5.10 | 2.583 | 0.722
[17 empty] | Y | 411.01 | 5.03 | 2.591 | 0.802
[17 empty] | B | 411.1 | 1.41 | 0.991 | 0.985
[17 empty] | Avg | 406.9 | 1.92 | 0.897 | 0.975
4 |  | Return Air |  | 65 |  |  |  |  | 1.1 |  |  |  | No | 24 | 353 | Belt | R | 414 | 1.56 | 0.887 | 0.815
[17 empty] | Y | 410.1 | 1.25 | 0.920 | 0.745
B
Avg
5 | B AHU 05 | Supply Air | 6000 | 100 |  |  |  |  | 5.5 |  |  |  | Schneider Yes 45 Hz | 24 | 353 | Belt | R | 410 | 2.49 | 1.708 | 0.990
[17 empty] | Y | 408 | 2.80 | 1.932 | 0.995
B
Avg
01 | PB ADV 01 | Supply Air | 800 | 125 | 800 OOD |  |  |  | 2.2 |  |  |  | No | 24 | 353 | Belt | R | 422.3 | 1.71 | 1.222 | 0.919
[17 empty] | Y | 427.7 | 1.60 | 1.107 | 0.887
B
Avg
| PB ADV 01 | Return Air | 800 | 75 | 200 BDB |  |  |  | 0.75 |  |  |  | No | 24 | 353 | Belt | R | 427.2 | 0.86 | 0.454 | 0.729
Y
B
Avg
03 | CP AHU 03 | Supply Air | 1700 | 100 | 846 @ 8000 |  |  |  | 15 |  |  |  | Yes ABB 42 Hz | 24 | 353 | Direct / Plug Fan | R | 425.8 | 10.2 | 6.612 | 0.923
Y
B
Avg
02 | B AHU 02 | Supply Air | 4000 | [5 empty] | 3.7 |  |  |  | Yes Biyoy | 24 | 353 | Belt | R | 410.1 | 5.03 | 2.901 | 0.81
[17 empty] | Y | 409.8 | 5.10 | 2.967 | 0.822
B
Avg
| B AHU 02 | Return Air | [6 empty] | 2.2 |  |  |  | Yes Biyoy / 24 | 24 | 353 | Belt | R | 406.3 | 2.37 | 1.565 | 0.940
[17 empty] | Y | 405.7 | 2.42 | 1.562 | 0.914
B
Avg
| B AHU 06 | Supply Air | 5000 | 100 |  |  |  |  | 37 |  |  |  | Yes Schneider 42Hz | 24 | 353 | Belt | R | 403.3 | 2.67 | 1.810 | 0.992
[17 empty] | Y | 400.5 | 2.72 | 1.742 | 0.988
B
Avg
|  | Return Air |  | 65 |  |  |  |  | 37 |  |  |  | Yes Schneider 50Hz | 24 | 353 | Belt | R | 403.5 | 3.15 | 2.143 | 0.991
[17 empty] | Y | 399.7 | 3.32 | 2.203 | 0.992
B
Avg
|  | Heater |  |  |  | Luban therm |  |  | 9 | [6 empty] | Thyristor | R | 403.8 | 9.93 | 6.496 | 0.972
[17 empty] | Y | 398.6 | 10 | 6.279 | 0.945
B
Avg
76 | FDV VS-02 |  | 5000 | 75 |  |  |  |  | 3.7 |  |  |  | NA DOL | 24 | 353 |  | R | 402.4 | 5.17 | 2.762 | 0.813
[17 empty] | Y | 401.8 | 5.29 | 2.784 | 0.798
B
Avg
77 | FDV NE-02 |  | 7000 | 75 |  |  |  |  | 5.5 |  |  |  | NA DOL | 24 | 353 |  | R | 403.6 | 6.53 | 4.110 | 0.876
[17 empty] | Y | 398.6 | 6.98 | 3.830 | 0.83
B
Avg
] | null | null | null | 85 | null | null | null | null | 3.7 | null | null | null | Yes, 32Hz, Schneider | 24 | 353 | Belt | R | 407.7 | 1.71 | 1.027 | 0.983
null | null | null | null | null | null | null | null | null | null | null | null | null | null | null | null | null | Y | 410 | 1.6 | 1.005 | 0.993
null | null | null | null | null | null | null | null | null | null | null | null | null | null | null | null | null | B | null | null | null | null
null | null | null | null | null | null | null | null | null | null | null | null | null | null | null | null | null | Avg | null | null | null | null
14 | B AHU | Supply Air | 1500 | 100 | null | null | null | null | 1.5 | null | null | null | Yes, 40Hz, Schneider | 24 | 353 | Belt | R | 405.7 | 1.75 | 1.122 | 0.854
null | null | null | null | null | null | null | null | null | null | null | null | null | null | null | null | null | Y | 403.2 | 1.8 | 1.006 | 0.795
null | null | null | null | null | null | null | null | null | null | null | null | null | null | null | null | null | B | null | null | null | null
null | null | null | null | null | null | null | null | null | null | null | null | null | null | null | null | null | Avg | null | null | null | null
null | null | Return Air | null | 65 | null | null | null | null | 1.1 | null | null | null | Yes, Schneider, 26 Hz | 24 | 353 | Belt | R | 402.0 | 0.45 | 0.257 | 0.914
null | null | null | null | null | null | null | null | null | null | null | null | null | null | null | null | null | Y | 406.4 | 0.42 | 0.231 | 0.891
null | null | null | null | null | null | null | null | null | null | null | null | null | null | null | null | null | B | null | null | null | null
null | null | null | null | null | null | null | null | null | null | null | null | null | null | null | null | null | Avg | null | null | null | null
10 | B AHU | Supply Air | 6000 | 100 | null | null | null | null | 5.5 | null | null | null | Yes, Danfoss, 36 Hz | 24 | 353 | Belt | R | 404.5 | 3.38 | 1.825 | 0.920
null | null | null | null | null | null | null | null | null | null | null | null | null | null | null | null | null | Y | 407.6 | 2.54 | 1.259 | 0.991
null | null | null | null | null | null | null | null | null | null | null | null | null | null | null | null | null | B | null | null | null | null
null | null | null | null | null | null | null | null | null | null | null | null | null | null | null | null | null | Avg | null | null | null | null
null | null | Return Air | null | 85 | null | null | null | null | 3.7 | null | null | null | Yes, Schneider, 27 Hz | 24 | 353 | Belt | R | 404.5 | 1.59 | 1.009 | 0.989
null | null | null | null | null | null | null | null | null | null | null | null | null | null | null | null | null | Y | 402.2 | 1.57 | 0.984 | 0.989
null | null | null | null | null | null | null | null | null | null | null | null | null | null | null | null | null | B | null | null | null | null
null | null | null | null | null | null | null | null | null | null | null | null | null | null | null | null | null | Avg | null | null | null | null
| B AHU 12 | Supply Air | 2000 | [5 empty] | 2.2 |  |  |  | Bypass | 24 | 353 |  | R | 406.5 | 2.46 | 1.307 | 0.729
[17 empty] | Y | 402.8 | 2.88 | 1.449 | 0.756
B
Avg
|  | Return Air | [6 empty] | 1.5 |  |  |  | Yes Schneider 39 Hz | 24 | 353 |  | R | 408.7 | 0.59 | 0.379 | 0.945
[17 empty] | Y | 409.3 | 0.59 | 0.368 | 0.954
B
Avg
| B AHU 04 | Supply Air | 10000 | [5 empty] | 11 |  |  |  | Yes Schneider 47 Hz | 24 | 353 |  | R | 414.3 | 7.89 | 5.081 | 0.933
[17 empty] | Y | 410.8 | 7.18 | 4.933 | 0.933
B
Avg
|  | Return Air | [6 empty] | 5.5 |  |  |  | Yes Schneider 27 Hz | 24 | 353 |  | R | 410.1 | 5.88 | 3.498 | 0.793
[17 empty] | Y | 411.8 | 5.76 | 3.790 | 0.849
B
Avg
SECTION: Equipment Nameplate (Format C)
Sr. | Equipment Name | Application | Make | Frame Size | Foot or Flange Mounted | Rated Power, KW | Rated Efficiency, % | IE Class (IE1/IE2/IE3) | Rated RPM | Direct Mount/ Pulley/ Gear | VFD installed, (Y/N), Oper Hz & Make | Daily Running Hours Hrs/Day | Annual Operating Days, Days/Year | Observations | Phase (R/Y/B/Avg) | Measured Voltage | Measured Current | Measured KW | Measured PF
1 | Aeration Blower 1 | STP | null | null | null | 3.7 | 86.30 | IE2 | 1440 | Belt | NO | 12 | 354 | Rated Discharge Pressure 0.4 kg/cm2 | R | 404.4 | 4.86 | 2.534 | 0.757
null | null | null | null | null | null | null | null | null | null | null | null | null | null | null | Y | 408.3 | 4.43 | 2.110 | 0.672
null | null | null | null | null | null | null | null | null | null | null | null | null | null | null | B | 408.9 | 4.55 | 2.181 | 0.678
null | null | null | null | null | null | null | null | null | null | null | null | null | null | null | Avg | null | null | null | null
2 | Aeration Blower 2 | STP | null | null | null | 3.7 | 86.30 | IE2 | 1440 | Belt | NO | 12 | 354 | null | R | null | null | null | null
null | null | null | null | null | null | null | null | null | null | null | null | null | null | null | Y | null | null | null | null
null | null | null | null | null | null | null | null | null | null | null | null | null | null | null | B | null | null | null | null
null | null | null | null | null | null | null | null | null | null | null | null | null | null | null | Avg | null | null | null | null
1 | Aeration Blower-1 |  |  |  | Foot | 11 | 89.8 | IE2 | 1460 | Belt | No | 12 | 365 |  | R | 404.4 | 11.7 | 6.842 | 0.822
[15 empty] | Y | 408.1 | 11.5 | 6.466 | 0.798
[15 empty] | B | 407.9 | 11.5 | 6.421 | 0.800
Avg
2 | Aeration Blower-2 |  |  |  | Foot | 11 | 89.8 | IE2 | 1460 | Belt | No | 12 | 365 |  | R
Y
B
Avg
3 | MBR Blower-1 |  |  |  | Foot | 5.5 | 87.7 | IE2 | 1450 | Belt | No | 12 | 365 | Discharge 0.45 kg/cm2 | R | 406.3 | 6.71 | 3.840 | 0.787
[15 empty] | Y | 403.4 | 6.48 | 3.959 | 0.856
[15 empty] | B | 407.6 | 6.40 | 3.969 | 0.886
Avg
4 | MBR Blower-2 |  |  |  | Foot | 5.5 | 87.7 | IE2 | 1450 | Belt | No | 12 | 365 | Discharge 0.45 kg/cm2 | R
Y
B
Avg
1 | 48 TR Secondary pump |  |  |  |  | 4 | 88.1 | [7 empty] | R
Y
B
Avg
2 | 33 TR Primary pump |  |  |  |  | 4 | 88.0 | [7 empty] | R
Y
B
Avg
3 | 33 TR Secondary pump |  |  |  |  | 4 | 88.1 | [7 empty] | R
Y
B
Avg
25 | 48 TR Chiller | Production | Blue Star | null | null | 80 | null | null | null | null | null | 24 | 365 | 15 days in month. Power factor is corrected as 3 capacitors are running. | R | 420 | 37.3 | 21.5 | 0.79
null | null | null | null | null | null | null | null | null | null | null | null | null | null | null | Y | 419.6 | 37.3 | 20.12 | 0.739
null | null | null | null | null | null | null | null | null | null | null | null | null | null | null | B | 414.9 | 35.5 | 21.75 | 0.763
null | null | null | null | null | null | null | null | null | null | null | null | null | null | null | Avg | null | null | null | null
26 | 44 TR Chiller | Production | Blue Star | null | null | 80 | null | null | null | null | null | 24 | 365 | 15 days in month | R | null | null | null | null
null | null | null | null | null | null | null | null | null | null | null | null | null | null | null | Y | null | null | null | null
null | null | null | null | null | null | null | null | null | null | null | null | null | null | null | B | null | null | null | null
null | null | null | null | null | null | null | null | null | null | null | null | null | null | null | Avg | null | null | null | null
34 | 34 TR | Production | null | null | null | null | null | null | null | null | null | 24 | 365 | 15 days in month | R | 414.9 | 61.3 | 33.37 | 0.759
null | null | null | null | null | null | null | null | null | null | null | null | null | null | null | Y | 411.9 | 64.8 | 35.83 | 0.772
null | null | null | null | null | null | null | null | null | null | null | null | null | null | null | B | 416.4 | 61.2 | 36.15 | 0.814
null | null | null | null | null | null | null | null | null | null | null | null | null | null | null | Avg | null | null | null | null
34 | 34 TR | Production | null | null | null | null | null | null | null | null | null | 24 | 365 | 15 days in month | R | null | null | null | null
null | null | null | null | null | null | null | null | null | null | null | null | null | null | null | Y | null | null | null | null
null | null | null | null | null | null | null | null | null | null | null | null | null | null | null | B | null | null | null | null
null | null | null | null | null | null | null | null | null | null | null | null | null | null | null | Avg | null | null | null | null
44 | 44 TR Primary pump | null | null | null | null | null | null | null | null | null | null | null | null | null | R | 422.8 | 6.77 | 4.518 | 0.910
null | null | null | null | null | null | null | null | null | null | null | null | null | null | null | Y | 421.6 | 6.49 | 4.182 | 0.982
null | null | null | null | null | null | null | null | null | null | null | null | null | null | null | B | null | null | null | null
null | null | null | null | null | null | null | null | null | null | null | null | null | null | null | Avg | null | null | null | null
1 | Pump 3 HP Pump | WTP-1 | Grundfos |  |  | 4 | 85.0 | IE2 | 2500 |  | No |  |  |  | R | 425.8 | 6.90 | 4.583 | 0.898
[15 empty] | Y | 425.5 | 6.89 | 4.559 | 0.897
[15 empty] | B | 426.0 | 6.89 | 4.558 | 0.896
Avg
2 | MCP Circul Pump | [13 empty] | R | 424.5 | 3.13 | 1.929 | 0.841
Y
B
Avg
16 | chiller 2 (200TR) U179 |  | York |  |  | 130.9 |  |  |  |  | No | 24 | 365 |  | R | 408.8 | 202 | 115.2 | 0.801
[15 empty] | Y | 410.9 | 203 | 116 | 0.800
[15 empty] | B | 408.8 | 202 | 115.2 | 0.805
Avg
| CT fan |  |  |  |  | 7.5 |  |  | 570 |  | No | 24 | 365 |  | R | 418.8 | 12.8 | 5.709 | 0.621
Y
B
[15 empty] | Avg | 408.5 | 13.4 | 6.085 | 0.639
| cooling tower pump-2 (condenser pump) |  |  |  |  | 30 |  |  | 1475 |  | No | 24 | 365 | 227.16 m3/hr, 27m, d-2.5 kg | R | 411.9 | 35.4 | 20.50 | 0.811
[15 empty] | Y | 411.9 | 35.9 | 20.99 | 0.811
[15 empty] | B | 410.2 | 37.8 | 22.60 | 0.834
Avg
| water circulation pump - 2 | [9 empty] | No | 24 | 365 | 125 m3/hr, 20m, S=2.4kg, d=4.5kg | R
Y
B
[15 empty] | Avg |  | 36
15 | Chiller (200 TR) | ARU | York | null | null | null | null | null | null | null | NO | 24 | 365 | U136 | R | 398.4 | 166 | 96.66 | 0.845
null | null | null | null | null | null | null | null | null | null | null | null | null | null | null | Y | 396.5 | 185 | 102.7 | 0.851
null | null | null | null | null | null | null | null | null | null | null | null | null | null | null | B | 399 | 176 | 103.9 | 0.845
null | null | null | null | null | null | null | null | null | null | null | null | null | null | null | Avg | null | null | null | null
16 | CT Fan (200 TR Chiller) | null | null | null | null | 7.5 | null | null | null | null | NO | 24 | 365 | null | R | 409.4 | 15.5 | 5.999 | 0.543
null | null | null | null | null | null | null | null | null | null | null | null | null | null | null | Y | 407.5 | 15.7 | 6.578 | 0.590
null | null | null | null | null | null | null | null | null | null | null | null | null | null | null | B | null | null | null | null
null | null | null | null | null | null | null | null | null | null | null | null | null | null | null | Avg | null | null | null | null
19 | Condenser pump for chiller 1 | Cooling Tower | null | null | null | 18.5 | null | null | 1440 | null | NO | 24 | 365 | 182 m3/hr, 26 m | R | 410.5 | 26.9 | 16.43 | 0.872
null | null | null | null | null | null | null | null | null | null | null | null | null | null | null | Y | 411.5 | 26.9 | 17.39 | 0.907
null | null | null | null | null | null | null | null | null | null | null | null | null | null | null | B | 411.3 | 26.8 | 17.27 | 0.907
null | null | null | null | null | null | null | null | null | null | null | null | null | null | null | Avg | null | null | null | null
17 | water circulation pump-2 | null | null | null | null | 22 | null | null | null | null | NO | 24 | 365 | 125 m3/hr, 40-20 m, 4.3 kg/cm2 discharge | R | 411.3 | 35.7 | 21.91 | 0.912
null | null | null | null | null | null | null | null | null | null | null | null | null | null | null | Y | 411 | 33.8 | 21.88 | 0.918
null | null | null | null | null | null | null | null | null | null | null | null | null | null | null | B | null | null | null | null
null | null | null | null | null | null | null | null | null | null | null | null | null | null | null | Avg | null | null | null | null
1 | Chiller 4 190 TR | [9 empty] | NO | 24 | 365 |  | R
Y
B
Avg
2 | CT Fan 200 TR | [9 empty] | NO | 24 | 365 |  | R | 428.6 | 8.25 | 3.630 | 0.579
[15 empty] | Y | 428.6 | 8.26 | 3.678 | 0.596
B
Avg
3 | condenser pump-1 |  |  |  |  | 15 KW |  |  | 2930 |  | NO | 24 | 365 | 180.9 m3/hr, 27m, 21.5, 1kg=10m | R | 430.9 | 17.8 | 11.12 | 0.833
[15 empty] | Y | 430.6 | 18.2 | 11.49 | 0.831
[15 empty] | B | 429.7 | 19.2 | 12.33 | 0.864
Avg
4 | Chilled water circulation pump-1 | [9 empty] | NO | 24 | 365 | 125 m3/hr, 30 m | R | 430.5 | 21.8 | 13.91 | 0.854
[15 empty] | Y | 430.2 | 21.7 | 13.95 | 0.859
B
Avg
1 | Chiller 3 | 100 TR | York | null | null | null | null | null | null | null | NO | 24 | 365 | CH3 VFD: 0 | R | 408.1 | 13.1 | 5.094 | 0.549
null | null | null | null | null | null | null | null | null | null | null | null | null | null | null | Y | 429.2 | 12.5 | 4.656 | 0.499
null | null | null | null | null | null | null | null | null | null | null | null | null | null | null | B | null | null | null | null
null | null | null | null | null | null | null | null | null | null | null | null | null | null | null | Avg | null | null | null | null
2 | CT fan | 250 TR | null | null | flange | 7.5 | null | null | 970 | null | NO | 24 | 365 | null | R | 409.9 | 18.1 | 12.42 | 0.987
null | null | null | null | null | null | null | null | null | null | null | null | null | null | null | Y | 426 | 18.3 | 13.39 | 0.994
null | null | null | null | null | null | null | null | null | null | null | null | null | null | null | B | null | null | null | null
null | null | null | null | null | null | null | null | null | null | null | null | null | null | null | Avg | null | null | null | null
3 | Cooling tower condenser pump - 2 | null | null | null | null | 18.5 | null | IE3 | 1480 | null | NO | 24 | 365 | 130 m3/hr 25 m | R | 429.9 | 26.2 | 19.67 | 0.733
null | null | null | null | null | null | null | null | null | null | null | null | null | null | null | Y | 428.1 | 26.3 | 19.70 | 0.729
null | null | null | null | null | null | null | null | null | null | null | null | null | null | null | B | null | null | null | null
null | null | null | null | null | null | null | null | null | null | null | null | null | null | null | Avg | null | null | null | null
4 | Water circulation pump-2 | null | null | null | null | 22.5 | null | null | null | null | NO | 24 | 365 | No pump name plate 5.8 kg discharge | R | null | null | null | null
null | null | null | null | null | null | null | null | null | null | null | null | null | null | null | Y | null | null | null | null
null | null | null | null | null | null | null | null | null | null | null | null | null | null | null | B | null | null | null | null
null | null | null | null | null | null | null | null | null | null | null | null | null | null | null | Avg | null | null | null | null
1 | Vacuum Pump No. 4 (710-730 mmHg) | null | null | null | null | 7.5 / 10 | null | null | 1450 | null | NO | 11:30 to 11:30 PM | 365 | regularly | R | 398.9 | 10.5 | 6.121 | 0.848
null | null | null | null | null | null | null | null | null | null | null | null | null | null | null | Y | 398.8 | 10.6 | 6.062 | 0.828
null | null | null | null | null | null | null | null | null | null | null | null | null | null | null | B | 396.1 | 11 | 5.725 | 0.762
null | null | null | null | null | null | null | null | null | null | null | null | null | null | null | Avg | null | null | null | null
1 | Air compressor CT tower |  |  |  |  | 3.7 |  |  |  |  | NO | 24 | 365 |  | R | 414.9 | 7.04 | 2.565 | 0.435
[15 empty] | Y | 424.4 | 6.88 | 2.515 | 0.523
[15 empty] | B | 420.9 | 7.16 | 2.715 | 0.512
Avg
2 | Air compressor cooling tower pump |  |  |  |  | 7.5 | [7 empty] | 92 m3/hr, 35 m, 2.4 kg disch | R | 419.8 | 6.72 | 2.845 | 0.719
[15 empty] | Y | 420 | 6.63 | 2.819 | 0.716
[15 empty] | B | 423.9 | 5.70 | 3.453 | 0.718
Avg
3 | Air compressor 405 CFM |  |  |  |  | 75 |  |  |  |  | Soft Starter | 24 | 365 | 6.8 bar Nedis | R | 424.7 | 8.68 | 5.103 | 0.794
[15 empty] | Y | 420.5 | 8.31 | 5.764 | 0.789
[15 empty] | B | 421.6 | 8.01 | 5.750 | 0.827
Avg
4 | Air dryer | Parker |  |  |  | 5.5 |  | IE2 |  |  | NO | 24 | 365 | 6.8 | R
Y
B
Avg
5 | Vacuum pump NO. 2 |  |  |  |  | 7.5 |  |  | 1450 RPM |  | NO | 6 am to 11 pm | 365 |  | R | 416.3 | 10.8 | 5.368 | 0.686
[15 empty] | Y | 417.7 | 10.9 | 5.426 | 0.678
[15 empty] | B | 416.7 | 10.7 | 5.318 | 0.687
Avg
SECTION: Pump/ETP Audit (Format D)
Sr. | Pump Name | Application | Design Flow (m3/hr) | Design Head (m) | Suction Pressure (kg/cm2) | Discharge Pressure (kg/cm2) | Measured Flow (m3/hr) | Make | Frame Size | Foot/Flange Mounted | Rated Power KW | Rated Efficiency % | IE Class | Rated RPM | VFD Details | Daily Running Hours | Annual Operating Days | Throttling Present (Yes/No) | Phase (R/Y/B/Avg) | Measured Voltage | Measured Current | Measured KW | Measured PF
1 | RAS Pump - 1 | ETP |  |  |  | 2 |  | APECC | 132 M | Foot | 5.5 | 86.0 | IE2 | 950 | N | 12 | 365 |  | R | 408 | 6.51 | 2.25 | 0.480
[19 empty] | Y | 405.1 | 6.57 | 2.11 | 0.462
[19 empty] | B | 403.1 | 6.38 | 2.5 | 0.497
Avg
2 | RAS Pump - 2 | ETP |  |  |  | 2 |  | APECC | 132 M | Foot | 5.5 | 86.0 | IE2 | 950 | N | 12 | 365 |  | R
Y
B
Avg
1 | PW Tank 1 Pump | [9 empty] | 7.5 |  |  |  | Yes, Power Flex |  |  |  | R | 421.3 | 6.36 | 7.827 | 0.917
[19 empty] | Y | 418.2 | 6.80 | 1.708 | 0.911
[19 empty] | B | 417.9 | 6.79 | 4.138 | 0.930
Avg
2 | PW Tank 2 | [9 empty] | 5.5 |  |  |  | Yes, 50 HZ, Power Flex |  |  |  | R | 433.8 | 7.29 | 4.913 | 0.922
[19 empty] | Y | 440.2 | 7.72 | 4.953 | 0.915
[19 empty] | B | 443.2 | 7.25 | 4.659 | 0.907
Avg
3 | WFI Tank 2 Pump | [9 empty] | 5.5 |  |  |  | Yes, 49.5 HZ, Power Flex |  |  |  | R | 437.5 | 7.52 | 4.669 | 0.903
[19 empty] | Y | 436.0 | 7.59 | 4.782 | 0.928
B
Avg
4 | HWTID PW Tank Pump | [9 empty] | 5.5 |  |  |  | Yes, Siemens |  |  |  | R | 391.9 | 4.82 | 1.522 | 0.596
[19 empty] | Y | 387.0 | 4.21 | 1.12 | 0.623
B
Avg
5 | HWTID WFI Tank Pump | [9 empty] | 5.5 |  |  |  | Yes, Siemens |  |  |  | R | 403.2 | 5.09 | 1.638 | 0.855
[19 empty] | Y | 398.8 | 5.35 | 1.424 | 0.994
[19 empty] | B | 402.4 | 4.86 | 1.709 | 0.869
Avg